Function code

0x03: Read data from the device registers

Master packets

Starting structure	Byte length of bus idle time
From the device address	1 Bytes and the contents 0-0xff
Function code	1 Bytes and the contents 3
Starting register address	2 Bytes, high byte first
Number of registers	2 Bytes, high byte first
CRC Checksum	2 Byte, low byte first
The end of the structure	4 Byte length of bus idle time

Response message from the station:

Normal operation when

Starting structure	4 Byte length of bus idle time
From the device address	1 Bytes and the contents 0-0xff
Function code	1 Bytes and the contents 3
Data length	1 Bytes, the number of registers × 2
Data	The number of registers × 2 bytes, each data high byte first
CRC Checksum	2 bytes, little endian
The end of the structure	4-byte length of bus idle time

Abnormal operation

Starting structure	4 Byte length of bus idle time
From the device address	1 Bytes and the contents 0-0xff
Function code	1 byte, 0x83
Data	Error code, as shown in Table 8.3 Error Codes Table
CRC Checksum	2 bytes, little endian
The end of the structure	4-byte length of bus idle time

0x10 : Write data from the device registers

Master packet:

Starting structure	4 Byte length of bus idle time
From the device address	1 Bytes and the contents 0-0xff
Function code	1 byte, 0x10
Starting register address	2 bytes, high byte first
Number of registers	2 bytes, high byte first
Data length	1 byte, the number of registers × 2
Data	The number of registers × 2 bytes, each data high byte first
CRC Checksum	2 bytes, little endian
The end of the structure	4-byte length of bus idle time

Response message from the station

Normal operation when

Starting structure	4 Byte length of bus idle time
From the device address	1 Bytes and the contents 0-0xff
Function code	1 byte, 0x10
Starting register address	2 bytes, high byte first
Number of registers	2 bytes, high byte first
CRC Checksum	2 bytes, little endian
The end of the structure	4-byte length of bus idle time

Abnormal operation

Starting structure	4 Byte length of bus idle time
From the device address	1 Bytes and the contents 0-0xff
Function code	1 byte, 0x90
Data	Error code, as shown in Table 8.3 Error Codes Table
CRC Checksum	2 bytes, little endian
The end of the structure	4-byte length of bus idle time

List of registers and floating-point value and the original value of the conversion formula

Register address	Number of	Register contents	Status	The range of data
0x0000	1	Module Model	Read-only	Module model configuration, for example, Such as: MDIA
0x0001	1	Module software version	Read-only	Such as 5.2, the high byte Major version, low byte times Version
0x0002	10	Module name	Read and write
0x000C	1	Module address	Read and write	0x0000-0x00FF
0x0501	1	Analog value of channel 0 (2-byte floating-point)	Read-only	Read analog value
0x0502	1	Analog value of channel 0 (2-byte floating-point)	Read-only	Read analog value
0x0503	1	Analog value of channel 1 (2-byte floating-point)	Read-only	Read analog value
0x0504	1	Analog value of channel 1 (2-byte floating-point)	Read-only	Read analog value
0x0505	1	Analog value of channel 2 (2-byte floating-point)	Read-only	Read analog value
0x0506	1	Analog value of channel 2 (2-byte floating-point)	Read-only	Read analog value
0x0507	1	Analog value of channel 3 (2-byte floating-point)	Read-only	Read analog value
0x0508	1	Analog value of channel 3 (2-byte floating-point)	Read-only	Read analog value
0x0509	1	Analog value of channel 4 (2-byte floating-point)	Read-only	Read analog value
0x050A	1	Analog value of channel 4 (2-byte floating-point)	Read-only	Read analog value
0x050B	1	Analog value of channel 5 (2-byte floating-point)	Read-only	Read analog value
0x050C	1	Analog value of channel 5 (2-byte floating-point)	Read-only	Read analog value
0x050D	1	Analog value of channel 6 (2-byte floating-point)	Read-only	Read analog value
0x050E	1	Analog value of channel 6 (2-byte floating-point)	Read-only	Read analog value
0x050F	1	Analog value of channel 7 (2-byte floating-point)	Read-only	Read analog value
0x0510	1	Analog value of channel 7 (2-byte floating-point)	Read-only	Read analog value
0x0511	1	Analog channel 0 input (raw value)	Read-only	0x0000-0xFFFF
0x0512	1	Analog channel 1 input (raw value)	Read-only	0x0000-0xFFFF
0x0513	1	Analog channel 2 input (raw value)	Read-only	0x0000-0xFFFF
0x0514	1	Analog channel 3 input (raw value)	Read-only	0x0000-0xFFFF
0x0515	1	Analog channel 4 input (raw value)	Read-only	0x0000-0xFFFF
0x0516	1	Analog channel 5 input (raw value)	Read-only	0x0000-0xFFFF
0x0517	1	Analog channel 6 input (raw value)	Read-only	0x0000-0xFFFF
0x0518	1	Analog channel 7 input (raw value)	Read-only	0x0000-0xFFFF
0x0519	1	The DI0 the value	Read-only	0x0000-0x0001
0x051A	1	The DI1 the value	Read-only	0x0000-0x0001
0x051B	1	The DI the value	Read-only	0x0000-0x0003

DI status (register 0x051B):

Data bit	Meaning
1	The state of the input channel 1, 0 is off, 1 is closed
0	The state of the input channel 0, 0 is off, 1 is closed